## Slide 1
PumpRupee
Pricing pump energy waste in rupees
A clamp-on audit kit that tells you if a VFD will pay back for THAT pump.
No flow meter
No shutdown
₹ waste by cause
Schneider Electric Yuva Yodha Energy Tech Hackathon 2026
Track: Smart Manufacturing
Electrify · Automate · Digitalise
Team ANS_4X
ESP32
logger
Motor
Pump
Power clamp (on motor cable)
Pressure transmitter
Throttle valve
Strainer + optional
2nd transmitter
All results are simulated (Grundfos NB 65-160/157, 11 kW). Prices are indicative online prices, not quotes.
Notes: 30 seconds: pumps are oversized and run throttled; the energy is burnt across the valve. Owners cannot see it because flow is hard to measure. PumpRupee is a clamp-on kit that prices the waste in rupees and says whether a VFD will pay back for that pump. It audits and recommends; it never controls the pump.

## Slide 2
Problem: Invisible Waste
Oversized pumps run throttled. The extra energy is burnt across a valve, every hour.
Oversized pump
Sized above the real duty
Valve half shut
Throttled to hold flow
Energy lost as heat
Head burnt in the valve
₹ leaking
On every bill
The owner is blind to it.
Flow is hard and costly to measure. An energy-audit practitioner reports that 30–40% of ultrasonic flow readings go wrong. Head (pressure) and electrical power are easy to measure.
Most common cause
Wrong sizing leads to throttling (practitioner report)
83–93%
of simulated waste is the valve (72–87% under stress)
8–45%
VFD saving across simulated cases; 5–40% reported in practice
Simulated figures: Grundfos NB 65-160/157, 11 kW. The 83–93% valve share is measured against a speed-matched, healthy, clean ideal.
Notes: The 5-40% is the practitioner's reported range; 8-45% is our simulated range across oversizing and lift cases. Keep the two separate.

## Slide 3
Why Today's Options Rarely Reach MSMEs
Each option is valuable. None is a low-cost entry point that ends in a ₹ decision.
Flow-meter retrofit
One-time manual audit
Full monitoring platform
PumpRupee
Upfront cost, small plant
Meter + install
Fee per visit
Typically higher
₹6,100–13,300
No plant shutdown
Answer in ₹
Waste split by cause
Pump-specific VFD verdict
Verifies saving afterwards
Suited to small MSMEs
✔ yes ~ partly / varies by product ✘ no. Our general assessment, not a product test. PumpRupee's ticks are design targets (simulated, not field-proven).
Full platforms are the natural NEXT step after PumpRupee, not a rival.
Notes: Fair comparison. Say clearly that platforms such as EcoStruxure are what an MSME graduates to once the audit has shown where the money is.

## Slide 4
Our Solution: A ₹ Audit Kit
A clamp-on kit turns power + pressure readings into “₹ wasted per year, and why”.
ESP32
logger
Motor
Pump
Power clamp (on motor cable)
Pressure transmitter
Throttle valve
Strainer + optional
2nd transmitter
₹ waste per year
Pump energy waste priced in rupees
Waste by cause
Valve, impeller wear, clogged strainer
Cheapest fix first + setpoint
Lowest safe VFD setpoint
VFD payback verdict
For THIS pump, before capex
VFD = control speed instead of strangling the pipe.
Audits and recommends. Does not control the pump.
Notes: The kit is read-only: clamp on the motor cable, sensors on existing gauge ports. The owner keeps the data.

## Slide 5
How It Works: Install & Pump Curve
Clamp on, log for a week or two, and let the maths find the waste.
Motor
Power clamp
(CT on cable)
Pump
P1 suction (optional)
P2 discharge
Throttle valve
P3 process-side
(optional)
Process
Minimum kit: power clamp + discharge pressure (P2).
Add P3 (process-side) when a VFD purchase is on the table: it measures the system curve and reveals a clogged strainer.
P2 + power Waste priced in ₹ (basic)
+ P3 (about ₹3,068) Error 10.5 → 1.4 pts (stress, simulated)
+ P1 / strainer ΔP Clog made visible
System curve = what the pipe network demands. Pump curve = what the pump can deliver at a given speed.
Throttled point vs VFD point (schematic)
Chart: Flow →
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Pump curve, full speed | 40 | 39.7 | 38.6 | 36.9 | 34.4 | 31.3 | 27.4 | 22.9
System, valve open | 12 | 12.1 | 12.5 | 13.1 | 13.9 | 15 | 16.3 | 17.9
System, throttled | 12 | 12.4 | 13.7 | 15.9 | 18.8 | 22.7 | 27.4 | 33
Pump curve, slowed by VFD | 28.9 | 28.6 | 27.5 | 25.8 | 23.3 | 20.2 | 16.3 | 11.8
Same flow, two ways to get it.
Throttled: pump pushes at full head, the valve burns the gap. VFD: the pump slows to just what the pipe needs. The gap is the wasted head, and it is priced in ₹.
Notes: Curves are schematic and illustrative shapes, not the Grundfos data. Real fits are in the simulation scripts.

## Slide 6
Analytics & Honest Accuracy
Six plain steps from raw logs to a ₹ report, with the uncertainty stated.
Raw logs
Power + pressure, 7–14 days
Calibration
Fit the real pump from its logs; optional anchors: shut-off head, closed-valve power
Flow inference
Pump curve + power + head give flow
Shapley split
A fair split of blame between causes
CUSUM check
Early alarm when the pump slowly wears
₹ report
₹/yr, SEC, fixes, setpoint. SEC = units of electricity per m³ pumped
Forecast error, percentage points (simulated)
Chart: 
| Datasheet | Logs | Logs + P3
Friendly test (1% noise) | 7.2 | 1.6
Stress test (3% noise, curve errors) | 8.4 | 10.5 | 1.4
The system curve, not the pump curve, is the main error source. A ±30% flow reading is worse than none (16.8 vs 8.3). About ±3 points only with a measured system curve; otherwise about ±10.
Wear-drift check (CUSUM), simulated
0
15
30
45
Day
6% step: caught next day
Fast wear: alarm ~day 22 at ≈3.7%
Slow wear (0→10% in 180 d): alarm ~day 40 at ≈2.2%
Wear caught at about 2–4%. 1 false alarm in 3 × 365 simulated days.
Notes: Friendly = 1% noise and exact system curve. Stress = 3% noise, curve-shape errors, wrong static lift/friction. The stress numbers are the honest ones. The learned-from-logs number gets WORSE under stress unless the system curve is measured; that is exactly why P3 exists.

## Slide 7
Results (Simulated)
SIMULATED – Grundfos NB 65-160/157, 11 kW, IE3
Assumed: 10 m static lift | 5% head margin | 16 h/day | 300 days/yr | ₹8/kWh | VFD efficiency 0.97 | 0.710 kg CO₂/kWh. Peak demand 90% of rated flow.
VFD, constant pressure
19.3% saved
₹69,292/yr | 6.1 t CO₂ | ≈8,660 kWh
VFD, proportional
35.5% saved
₹1,27,178/yr | 11.3 t CO₂ | ≈15,900 kWh
Chart: Energy saving, %
| Constant pressure | Proportional pressure
Base case (peak 90%, 10 m lift) | 19.3 | 35.5
Right-sized pump, 20 m lift | 8 | 15
Range: 8–33% (constant), 15–45% (proportional). 54–60% for heavily oversized pumps is an upper bound only. ₹, kWh and CO₂ are consistent: kWh = ₹ ÷ 8; CO₂ = kWh × 0.710 (arithmetic).
Where the waste goes
Chart: 
| Valve (throttling) | Wear, clog, other
Waste | 83 | 17
≥83%
Valve share 83–93%
(72–87% under stress). Donut shows the low end. Measured against a speed-matched, healthy, clean ideal.
Clog blind spot
A clogged strainer is invisible with power + pressure alone. One extra pressure sensor recovers about ₹6,000–6,600/yr of misattributed waste.
Notes: Per-pump numbers are simulated. kWh derived as rupees divided by 8; CO2 as kWh times 0.710: 69,292/8 = 8,661 kWh -> 6.1 t; 1,27,178/8 = 15,897 kWh -> 11.3 t.

## Slide 8
Cost & VFD Verdict
INDICATIVE ONLINE PRICES, NOT QUOTES
Bill of materials (preliminary)
ESP32 dev board
₹399–449
Power clamp, SCT-013 100 A
₹349 + GST to ₹729
Voltage sensor ZMPT101B
₹92–289
Pressure transmitter, basic
₹2,100–3,068
Enclosure, supply, 4–20 mA, wiring
₹2,000 (assumed)
Basic single-phase
≈ ₹6,100
3-phase + 2nd transmitter
≈ ₹10,200
3-phase + process-side (P3)
≈ ₹13,300
With ₹12,000 transmitters
≈ ₹40,100
Hobby-grade clamps; not a certified meter. Volume cost: not estimated (no quotes).
Value per pump
Cost per pump audited
Kit ÷ N pumps. N = 10: ₹610–1,330
Audit time per pump
Install (assumed ½ day) + 7–14 days logging + report
Kit throughput
About 25–50 pumps/yr per kit at 7–14 days each (arithmetic, excludes travel)
Kit payback
₹10,200 ≈ 1.8 months of the base-case saving of ₹69,292/yr, if the audit leads to that VFD (illustrative)
VFD verdict (simulated)
Oversized pump
4–19 months
GO: buy the VFD
Right-sized, high lift
2–4+ years
WAIT: fix cheaper things first
VFD ₹29,000–94,000 + about ₹15,000 install (assumed): ₹50,200–1,09,400 in total.
A ~₹10k kit can stop a wrong ₹50k–1.1 lakh VFD buy, or unlock ₹69,292–1,27,178/yr (simulated)
Notes: Arithmetic: 6,100/10 = 610 and 13,300/10 = 1,330. 365/14 = 26 and 365/7 = 52. 10,200/69,292 = 0.147 yr = 1.8 months. The kit payback is illustrative because it assumes the audit leads to the base-case VFD.

## Slide 9
Ecosystem Fit: Audit → Drive → Verify
PumpRupee is the low-cost front door to VFD and energy-management adoption.
Electrify
Makes motor electrical energy visible with a clamp-on power measurement and points owners to efficient drives.
Automate
Shows which pumps justify a drive and the lowest safe setpoint. The drive does the controlling; PumpRupee never does.
Digitalise
Logs become a ₹ business case and a before/after proof. The owner keeps the data and can use any drive.
1
PumpRupee audit
Clamp-on, 7–14 days
2
₹ business case
Waste by cause + VFD verdict
3
VFD installed
e.g. Altivar Process
4
PumpRupee re-measures
Same kit, after the fix
5
Verified saving
Feeds energy management, e.g. EcoStruxure
Why this helps drive and EMS adoption
MSMEs that skip audits today get a ₹ case they understand, a pump-specific verdict before capex, and proof after.
Smart Manufacturing fit
Energy efficiency · productivity · digitalisation · sustainability
Concept only: no drive or platform integration built.
Notes: Schneider products are named only as examples of where an audited MSME goes next. No integration claim.

## Slide 10
Ease of Use & Safety
Clamp → Fit → Log → Read ₹ report → Fix → Verify.
1
Clamp
On the motor cable
2
Fit
Sensors on gauge ports
3
Log
7–14 days
4
Read
₹ report
5
Fix
Cheapest first
6
Verify
Re-measure
7
Move
Kit to next pump
The owner or technician does NOT need
A flow meter
Pipe cutting
Production shutdown
Hydraulic expertise
Reading graphs
Safety & reliability by design
Non-invasive power clamp
Pressure sensors on existing gauge ports
Rated enclosure; installed by a plant electrician
Kit only recommends, never controls the pump
Owner keeps the data
Closed-valve power / shut-off head anchors are optional, brief, and within the pump maker's limits.
Notes: The workflow is a design intent. No hardware has been field-tested yet.

## Slide 11
Impact, Scalability & Roadmap
IMPACT = SIMULATED, per 11 kW pump
₹69k–1.27 lakh
per year
≈8,660–15,900
kWh per year
6.1–11.3
t CO₂ per year
Scale-up illustration, not a projection: N pumps × per-pump saving. N = 10: ₹6,92,920–12,71,780/yr and 61–113 t CO₂/yr.
Scalability
Single pump
Plant (shared kit)
Cluster / ESCO / channel partner
Bundled with VFD & EMS offers
Applications: MSME factories, water utilities, textile/dyeing, food processing, commercial HVAC chilled-water pumps. Agricultural pumping: future scope only.
Roadmap
1. Simulation
DONE
2. Bench test, real pump + sensors
NEXT
3. Pilot, 1–2 plants, measured system curve
PLANNED
4. Validate forecast error
PLANNED
5. Multi-pump / multi-plant rollout
PLANNED
Validation status
SIMULATED / DESIGNED
Savings, waste split, calibration, drift detection, cost estimates
TO BE TESTED
Flow inference vs a reference meter; throttled-valve and blocked-strainer cases; wear drift; pilots; before/after VFD saving
Notes: ACTUALLY TESTED: nothing yet, no hardware or field data. Say this out loud.

## Slide 12
PumpRupee on One Page
Cheap kit. Clever inference. Answers in rupees. Honest about limits.
Oversized pump, throttled valve
Clamp-on kit
₹6,100–13,300
₹ report by cause
VFD verdict
GO or WAIT
Verified before/after saving
19.3–35.5%
VFD saving, base case
₹69,292–1,27,178
per year, per 11 kW pump
4–19 mo vs 2–4+ yr
payback: oversized vs right-sized
≈ ±3 points
only with a measured system curve; else ≈ ±10
All SIMULATED (Grundfos NB 65-160/157, 11 kW; 10 m lift, 5% margin, 16 h/day, 300 days, ₹8/kWh).
Honest limits: what we validate next
Simulation only: no lab/field data, no real quotes
System-curve fit uses the simulated plant's own form, so it is optimistic
Single pump, steady state. Out of scope: parallel pumps, closed loops, pumps already on drives, minimum-flow/NPSH, control dynamics
Part of the valve share is by construction; 54–60% is an upper bound
Notes: Close with: cheap kit, clever inference, answers in rupees, honest about limits, brings VFD savings to MSMEs that never get audited.