## Slide 1
PumpRupee
Find the rupees your pumps waste, before you buy a VFD
No flow meter
No shutdown
₹ waste by cause
Team ANS_4X
Schneider Electric Yuva Yodha Energy Tech Hackathon 2026
Track: Smart Manufacturing · Electrify · Automate · Digitalise
Live prototype dashboard
https://pumprupee-dashboard.vercel.app/
Simulated data · scan the QR code
pumprupee-dashboard.vercel.app
Working prototype dashboard · simulated data
All results are simulated (Grundfos NB 65-160/157, 11 kW). Prices are indicative, not quotes.
Notes: Open the live dashboard from the QR code. Simulated data throughout. One sentence: PumpRupee tells an MSME owner how many rupees a pump wastes, why, and whether a VFD will pay back for that pump, using a cheap clamp-on kit and no flow meter.

## Slide 2
Problem Statement
Oversized pumps run throttled. The extra energy is burnt across a valve, every hour, and nobody sees it.
Oversized pump
Sized above the real duty
Valve half shut
Throttled to hold flow
Energy lost as heat
Head burnt in the valve
₹ leaking
On every bill
You pay for the pump AND for fighting the valve.
Oversizing is common
An energy-audit practitioner: wrong sizing leading to throttling is the most common cause.
Flow is hard to measure
Ultrasonic meters: 30–40% of readings go wrong (practitioner report). Pressure and power are easy.
Audits miss small plants
Full audits are a poor fit for small plants; very small plants rarely prioritise this.
Head (pressure) and electrical power are cheap to measure. Flow is not. PumpRupee infers flow from the two that are.
Notes: Anchor on the owner being blind. The 30-40% figure is an audit practitioner's report about ultrasonic meters, not our measurement.

## Slide 3
Proposed Solution
A clamp-on kit and a web dashboard turn power + pressure into “₹ wasted per year, and why”.
ESP32
logger
Motor
Pump
Power clamp (on motor cable)
Pressure transmitter
Throttle valve
Strainer + optional
2nd transmitter
Concept illustration of the kit on a pump skid
pumprupee-dashboard.vercel.app
Working prototype dashboard · simulated data
₹ waste per year, by cause
Cheapest fix first + safe setpoint
VFD payback verdict for THIS pump
Verified saving after the fix
Clamp on → log 7–14 days → ₹ report → the right fix
Audits and recommends. Does not control the pump.
Notes: The dashboard shown is the working prototype with simulated data. The kit is clamp-on: no pipe cutting, no shutdown. It never controls the pump.

## Slide 4
Alignment to Smart Manufacturing
Electrify · Automate · Digitalise, at an entry cost an MSME can afford.
Electrify
Makes motor energy visible with a clamp-on power measurement
Points owners to the pumps where a right-sized drive pays back
Automate
Automatic diagnosis of waste by cause
Wear-drift alarm (CUSUM) on the pump
Lowest safe VFD setpoint; the drive does the controlling
Digitalise
Logs become a ₹ business case on a dashboard
Before/after proof of the saving
Owner keeps the data and can use any drive
How PumpRupee feeds drives and energy management
1
PumpRupee audit
Clamp-on, 7–14 days
2
₹ business case
Waste by cause + VFD verdict
3
VFD installed
e.g. Altivar Process
4
PumpRupee re-measures
Same kit, after the fix
5
Verified saving
Feeds energy management, e.g. EcoStruxure
A low-cost front door that expands VFD and energy-management adoption into MSMEs that skip audits today. Concept only: no drive or platform integration built.
Notes: Schneider products are named only as the natural next step after an audit. Say it positively: PumpRupee finds which pumps justify an Altivar-class drive.

## Slide 5
Key Features & User Journey
Seven steps from clamp-on to a verified saving.
Clamp on Power clamp on the motor cable
Fit sensors Pressure on existing gauge ports
Log 7–14 days ESP32 records power + pressure
Open the dashboard ₹ report by cause
Apply the fix Cheapest first; VFD verdict
Re-measure Verify the saving
Move the kit Next pump
₹ waste by cause
No flow meter
No shutdown
VFD verdict
Verified savings
Reusable kit
Live prototype dashboard
https://pumprupee-dashboard.vercel.app/
Simulated data · scan the QR code
pumprupee-dashboard.vercel.app
1
2
3
Working prototype dashboard · simulated data
1
₹ saving per year with a VFD (simulated)
2
VFD payback range
3
Cheapest fix first, with the safe setpoint
Notes: Walk the numbered callouts on the dashboard: 1 the rupee saving, 2 the payback range, 3 the cheapest-fix-first order. Everything shown is simulated.

## Slide 6
Technical Approach
Motor
Power clamp
Pump
P1 suction (opt.)
P2 discharge
Throttle valve
P3 process side
(optional)
Process
Minimum kit: clamp + P2. Add P3 before a VFD purchase.
Logs
Calibrate
Infer flow
Shapley split
CUSUM check
₹ report
Shapley = fair split of blame between causes. CUSUM = early alarm when the pump slowly wears. SEC = electricity units per m³ pumped.
Grundfos NB 65-160/157 curves (fit to maker data)
Chart: Flow, m³/h
| 10 | 20 | 30 | 40 | 50 | 60 | 70
Pump, full speed | 33.1 | 33 | 32.8 | 32.6 | 32.3 | 31.8 | 31.2
System, valve open (assumed 10 m lift) | 10.1 | 10.5 | 11.1 | 12 | 13.1 | 14.5 | 16.1
System, throttled | 10.6 | 12.3 | 15.2 | 19.2 | 24.3 | 30.7 | 38.1
Pump slowed by VFD (72%) | 17.1 | 17 | 16.8 | 16.5 | 16.1 | 15.5 | 14.7
At an off-peak 61.6 m³/h the throttled pump delivers 31.7 m; the pipe needs 15.4 m. The gap is priced in ₹. Simulated; system curve assumed.
pumprupee-dashboard.vercel.app
1
2
3
Working prototype dashboard · simulated data
1
14 days of ESP32 logs (simulated playback)
2
Flow inferred from curve + power + head
3
Calibration error vs study mean
About ±3 points only with a measured system curve; otherwise about ±10.
Notes: Calibration: two scale factors (head, power) are fitted from 7-14 days of logs by profile likelihood; no flow meter. The system curve is the biggest error source, which is why the optional P3 sensor exists.

## Slide 7
Prototype & Simulated Results
SIMULATED – Grundfos NB 65-160/157, 11 kW · 10 m lift · 5% margin · 16 h/day · 300 days · ₹8/kWh
pumprupee-dashboard.vercel.app
1
2
3
Working prototype dashboard · simulated data
pumprupee-dashboard.vercel.app
1
2
3
Working prototype dashboard · simulated data
1
Valve is the largest share of waste
2
₹/yr attributed to the wrong cause, by sensor tier
3
Valve share is partly by construction
1
GO / NO-GO verdict for this pump
2
Annual saving in ₹
3
Break-even month
₹69,292 / ₹1,27,178
per year (constant / proportional)
83–93%
of waste is the valve
4–19 months
VFD payback, oversized pump
±3 / ±10 pts
with / without measured system curve
Notes: Screenshots are from the working prototype dashboard, simulated data. Forecast error: 1.4 points with a process-side sensor vs 10.5 points without, under stress. A +/-30% flow reading is worse than no calibration.

## Slide 8
Innovation
We build on proven tools. The new part is the integration for MSMEs.
Already exists (we build on it)
KSB PumpMeter, US DOE PSAT
Samotics (motor-current efficiency)
Schneider Altivar Process (sensorless flow), EcoStruxure
Indian IoT vendors and ESCOs
Shapley split and CUSUM: known methods
Our integration
₹ waste split by cause
Prices the value of an extra sensor
Low-cost shared kit, no flow meter
Built-in before/after verification
Pump-specific VFD verdict before capex
Flow meter
Manual audit
Full platform
PumpRupee
Upfront cost, small plant
Meter + install
Fee per visit
Higher
₹6,100–13,300
No shutdown
Answer in ₹
Cause breakdown
VFD verdict
Verified savings
Fits small MSMEs
✔ yes ~ partly / varies ✘ no. Our general assessment; PumpRupee's ticks are design targets (simulated).
We found no low-cost shared kit that combines these. Full platforms are the next step after PumpRupee.
Notes: Never say 'none exists'. Altivar Process does sensorless flow inside the drive after it is bought; PumpRupee helps decide which pumps deserve one and verifies the saving.

## Slide 9
Expected Impact
SIMULATED – per 11 kW pump; prices indicative, not quotes
A one-time kit vs a yearly saving (₹)
Kit, one-time and reusable (top tier)
₹13,300
Saving per year, constant pressure
₹69,292
Saving per year, proportional pressure
₹1,27,178
One kit ≈ 5–19% of a year's simulated saving on one pump.
6.1–11.3 t
CO₂ avoided per pump per year (0.710 kg/kWh)
₹50,200–1,09,400
wrong VFD purchase avoided where it won't pay back
4–19 months
payback, oversized pump (2–4+ years if right-sized, high lift)
Who benefits
MSME plant owners
Maintenance teams
Energy auditors / ESCOs
Drive channel partners
India's industrial efficiency goals
Scale-up illustration, not a projection: total = N pumps × per-pump saving. For N = 10: ₹6,92,920–12,71,780 per year and 61–113 t CO₂ per year, using the 11 kW base case. The 54–60% saving for heavily oversized pumps is an upper bound only.
Notes: 5-19% = 6,100/127,178 = 4.8% up to 13,300/69,292 = 19.2%. N=10 is arithmetic, not a forecast.

## Slide 10
Implementation Roadmap
What is done, what is next, and which limit each phase removes.
1
Simulation + dashboard
Real Grundfos curve fits, stress tests, working web dashboard (simulated data).
Limit removed: none yet
DONE
2
Bench test
Real pump, ESP32 kit and a reference flow meter.
Removes: flow-inference accuracy, head = discharge − suction
NEXT
3
Pilot, 1–2 plants
Measure the system curve on site; log 7–14 days.
Removes: ±10 → ±3 points
PLANNED
4
Validate forecast
Compare the forecast with the measured saving after a fix.
Removes: optimistic system-curve fit
PLANNED
5
Rollout
Multi-pump, multi-plant; ESCO and channel use.
Widens: parallel pumps, drives, NPSH
PLANNED
Honest limits we validate next
Simulation and software prototype only: no lab or field data, no real quotes
About ±3 points only with a measured system curve; otherwise about ±10; the curve fit is optimistic
Single pump, steady state. Out of scope: parallel pumps, closed loops, pumps already on drives, min-flow/NPSH, control dynamics
Notes: Lead with 'done' and 'next'. Ask: a pilot plant and a reference flow meter.

## Slide 11
Team Introduction
Team ANS_4X · Schneider Electric Yuva Yodha 2026 · Smart Manufacturing
Insert
photo
Akshaya V G
Team Lead & Software/Dashboard
Data pipeline and the PumpRupee web dashboard
Insert
photo
Adithyaa J
Embedded Hardware
ESP32 logger, power clamp and pressure-sensor integration
Insert
photo
Nikilaesh B
Energy Analytics
Pump hydraulics model, Shapley waste split and VFD payback logic
Insert
photo
Siva Subramaniam S
Simulation & Validation
Pump-curve simulation, CUSUM wear-drift testing, pilot and roadmap planning
Live prototype dashboard
https://pumprupee-dashboard.vercel.app/
Simulated data · scan the QR code
Cheap kit. Clever inference. Answers in rupees.
Notes: Close: cheap kit, clever inference, answers in rupees. Share the live link.