## Slide 1
PumpRupee
Pricing pump energy waste in rupees
A low-cost, clamp-on audit kit. No flow meter.
No flow meter
Clamp-on
₹ waste by cause
Challenge 04 – Smart Manufacturing
Yuva Yodha | Schneider Electric Energy Tech Hackathon
[Team name] | [Institution]
ESP32
logger
Motor
Pump
Power clamp (on motor cable)
Pressure transmitter
Throttle valve
Strainer + optional
2nd transmitter
All results in this deck are simulated (Grundfos NB 65-160/157, 11 kW). Prices are indicative, not quotes.
Notes: 30-second pitch: oversized pumps run throttled and burn energy across a valve. Owners can't see it because flow is hard to measure. PumpRupee is a clamp-on kit (power + pressure) that prices the waste in rupees, splits it by cause, and tells you if a VFD pays back for YOUR pump. Audits and recommends; does not control the pump.

## Slide 2
Problem Statement
Pumps are oversized and run throttled, so energy is burnt across a valve every hour.
Oversized pump
Sized above the real duty
Valve half shut
Throttled to hold flow
Energy lost as heat
Head burnt in the valve
₹ meter spinning
Paid on every bill
You pay for the pump AND for fighting the valve.
Owners can't see it because flow is hard to measure: an energy-audit practitioner reports that 30–40% of ultrasonic flow readings go wrong.
Existing approaches, and where each fits
Flow-meter retrofit
Fits: a direct flow reading.
Falls short: meter cost and installation; ultrasonic readings misread 30–40% (practitioner report).
Full ESCO audit
Fits: expert judgement and a trusted baseline.
Falls short: a point-in-time exercise and costly, not continuous.
Vendor platforms
Fits: deep integration with the vendor's own equipment.
Falls short: often vendor-locked or subscription-based.
PumpRupee
Fits: ₹ waste by cause at ₹6,100–13,300 per kit; no flow meter.
Limit: audits only, and results are simulated so far.
Notes: Be fair to alternatives: flow meters, ESCO audits and vendor platforms each have a place. PumpRupee's gap: continuous, low-cost, vendor-neutral, and prices waste by cause.

## Slide 3
Proposed Solution
A clamp-on kit turns power + pressure readings into “₹ wasted per year, and why”.
ESP32
logger
Motor
Pump
Power clamp (on motor cable)
Pressure transmitter
Throttle valve
Strainer + optional
2nd transmitter
₹ waste per year
The pump's energy waste priced in rupees
Waste by cause
Valve, impeller wear, clogged strainer
Ranked fixes + setpoint
Cheapest fix first; lowest safe VFD setpoint
Verified saving
Re-measure after the fix
Audits and recommends. Does not control the pump.
Notes: Hardware: ESP32 logger, power clamp on the motor cable, pressure transmitter on the discharge, optional second transmitter at the strainer / process side. No pipe cutting for the clamp.

## Slide 4
Alignment to Challenge 04 – Smart Manufacturing
Asset-level energy visibility, priced in rupees, at MSME entry cost.
Challenge goal
PumpRupee feature
Energy visibility at the asset level
SEC (kWh/m³) and ₹/m³ for each pump, plus the waste split by cause
Data-driven maintenance
CUSUM wear-drift alarm (wear caught at about 2–4%); strainer clog made visible with one extra pressure sensor
Measurable kWh and CO₂ reduction
Before/after re-measurement; CO₂ at 0.710 kg/kWh (CEA); simulated 6.1–11.3 t CO₂/yr per 11 kW pump
Low-cost entry for MSMEs
Clamp-on kit from readily available parts, about ₹6,100–13,300; no flow meter
Notes: Challenge goals are our reading of 'Smart Manufacturing': visibility, maintenance, measurable savings, accessible to MSMEs.

## Slide 5
Key Features & User Journey
From clamp-on to a verified saving, in seven steps.
1
Clamp on
No pipe cutting
2
Log 7–14 days
Power + pressure
3
Get ₹/yr report
Split by cause
4
Cheapest fix first
Valve, setpoint, strainer
5
Decide on VFD
Payback estimate
6
Re-measure
Verify the saving
7
Keep monitoring
Wear-drift alarm
Owner report: Pump P-01
EXAMPLE LAYOUT | SIMULATED VALUES
Waste by cause
Valve 83–93% of the waste; wear and clog share the rest
Top fixes, in order
1. Strainer, grease, alignment (cheap) 2. Speed control or impeller trim (largest saving)
Recommended setpoint
24.2 m (2.37 bar), constant pressure
VFD saving
19.3% = ₹69,292/yr, 6.1 t CO₂/yr
VFD payback
8.7–18.9 months. Example verdict: worth buying
No flow meter
Flow inferred from pump curve, power and head
Clamp-on install
Off-the-shelf parts, no pipe cutting
VFD verdict before you buy
Payback for YOUR pump
Before/after verification
Re-measure after the fix
Wear-drift alarm
Catches slow impeller wear
Notes: The report is the product. Values shown are the simulated base case (peak demand 90% of rated flow), not field data.

## Slide 6
Technical Approach: Architecture & Method
Sensors → ESP32 logger → calibration & analysis → owner report.
1. Sensors
Power clamp (+ voltage sensor)
Discharge pressure transmitter
Optional strainer / process-side transmitter
2. ESP32 logger
Logs power + pressure
Keeps 7–14 days of records
Clamp-on, no pipe cutting
3. Calibration & analysis
Flow from pump curve
Calibrate from logs
Shapley split
CUSUM wear drift
4. Owner report
₹/yr waste, SEC kWh/m³, ₹/m³
Ranked fixes + setpoint
Re-measure to verify
Method in plain words
Flow without a meter
Pump curve + logged power + head give an estimate of flow.
Calibration
Learn from 7–14 days of logs. Optional anchors: shut-off head, closed-valve power.
Shapley split
A fair way to share the blame among valve, wear and clog.
CUSUM drift
An alarm that notices slow drift, such as impeller wear.
SEC
Units of electricity per m³ pumped (kWh/m³).
Flow is inferred, never measured. A bad flow reading (±30%) is worse than no calibration, so PumpRupee does not depend on one.
Notes: Be ready to explain: Shapley split = average each cause's contribution over all orders in which causes could be removed.

## Slide 7
Technical Approach: Simulated Validation
SIMULATED – Grundfos NB 65-160/157, 11 kW, IE3
Assumed: 10 m static lift | 5% head margin | 16 h/day | 300 days/yr | ₹8/kWh | VFD efficiency 0.97 | 0.710 kg CO₂/kWh (CEA)
Where the waste goes
Forecast accuracy
Wear-drift detection
Valve (throttling) share of waste
83–93%
Rest: wear, clog, other. Under stress tests the valve share is 72–87%. Measured against a speed-matched, healthy, clean ideal.
Clog blind spot
A clogged strainer is invisible with power + pressure alone. One extra pressure sensor recovers about ₹6,000–6,600/yr of misattributed waste.
Chart: 
| Datasheet | Learned (logs) | + process sensor
Friendly test (1% noise) | 7.2 | 1.6
Stress test (3% noise, curve errors) | 8.4 | 10.5 | 1.4
Mean error, percentage points.
The system curve, not the pump curve, is the main error source. A ±30% flow reading is worse than none (16.8 vs 8.3).
About ±3 points only with a measured system curve; else about ±10.
0
15
30
45
Day (simulated)
6% step in wear: caught the next day
Fast wear: alarm ~day 22 at ≈3.7% wear
Slow wear (0→10% in 180 days): alarm ~day 40 at ≈2.2% wear
Wear caught at about 2–4%
1 false alarm in 3 × 365 simulated days
Notes: Everything on this slide is simulation. Friendly = 1% noise, curves a scaled copy of the datasheet, exact system curve. Stress = 3% noise, curve-shape errors, wrong static lift/friction. We report the stress numbers because they are the honest ones.

## Slide 8
Innovation: System-Level Packaging
We do not claim pump monitoring, sensorless flow or VFD savings are new.
Existing technology (we build on it)
KSB PumpMeter pump monitoring
US DOE PSAT pump energy assessment tool
Samotics motor-current pump efficiency
Schneider Altivar Process sensorless flow in the drive
Indian IoT vendors, ESCOs monitoring and audits
Our integration
₹/year waste split by cause, not just an efficiency number
Prices the extra sensor that would reveal what the basic kit cannot see
Low-cost shared audit kit with no flow meter
Before/after verification built in
A VFD payback verdict for the owner's own pump
We found no low-cost shared kit that combines all four. (A search result, not proof that none exists.)
Notes: Never say 'no such solution exists'. Say what we searched and what we did not find.

## Slide 9
Expected Impact: Savings & Cost
SIMULATED – per 11 kW pump, peak demand 90% of rated flow
VFD, constant pressure
19.3% saved
₹69,292/yr | 6.1 t CO₂/yr
VFD, proportional pressure
35.5% saved
₹1,27,178/yr | 11.3 t CO₂/yr
Chart: Energy saving, % (simulated)
| Constant pressure | Proportional pressure
Base case (peak 90%, 10 m lift) | 19.3 | 35.5
Right-sized pump, 20 m lift | 8 | 15
Range across cases: 8–33% (constant), 15–45% (proportional). Heavily oversized pumps reach 54–60% in the model: an upper bound only. An energy-audit practitioner reports 5–40% in practice.
Cost & payback (indicative prices)
Basic single-phase
₹6,100
3-phase + 2nd transmitter
₹10,200
3-phase + process-side transmitter
₹13,300
With ₹12,000 industrial transmitters
₹40,100
VFD for 11 kW: ₹29,000–94,000 + ₹15,000 install (assumed)
VFD payback (simulated)
Oversized pump
4–19 months
Right-sized, high lift
2–4 years+
The audit tells you which case you are in BEFORE you spend on a VFD.
Audit kit cost is shared across pumps and is not included in the payback.
Who benefits: MSME plant owners, maintenance teams, energy auditors. Scale-up (illustration, not a projection): N pumps × per-pump saving. For N = 10 on the base case: ₹6,92,920/yr and 61 t CO₂/yr (constant pressure).
Notes: Per-pump savings are from the simulated model with the stated assumptions. The N = 10 line is arithmetic (10 x 69,292 and 10 x 6.1), not a forecast.

## Slide 10
Implementation Roadmap
From a simulated result to a field-validated audit kit.
1
Simulation
Real Grundfos NB 65-160/157 curves; stress-tested
DONE
2
Bench test
Real pump and sensors; check inferred flow and calibration
NEXT
3
Pilot, 1–2 plants
Measure the system curve; log 7–14 days
PLANNED
4
Validate error
Compare forecast error with the ±3-point claim
PLANNED
5
Rollout
Multi-pump, multi-plant
PLANNED
What we validate next (honest limits)
Simulation only: no lab or field data yet, and no real quotes
About ±3 points only with a measured system curve; otherwise about ±10
The system-curve fit uses the same form as the simulated plant, so it is optimistic
Single pump, steady state, hourly. Next: parallel pumps, closed loops, pumps already on drives, minimum-flow and NPSH checks, control dynamics
Notes: Present limits as the validation plan. Judges trust a team that states what it has not yet proven.

## Slide 11
Team Introduction
[Team name] | [Institution]
[Name]
[Role]
[Skill: one line relevant to pumps, sensors, data or energy]
[Name]
[Role]
[Skill: one line relevant to pumps, sensors, data or energy]
[Name]
[Role]
[Skill: one line relevant to pumps, sensors, data or energy]
[Name]
[Role]
[Skill: one line relevant to pumps, sensors, data or energy]
Replace the photo circles and [placeholders]; delete unused cards (1–4 members).